Daylight Architecture for Control System

Dialight Architecture for Control System

(DACS)

User Guide

V1.2

Contents

Introduction	3

Technical Specifications	4

System Architecture Overview	5

Control Systems Overview	11

Control Systems Overview continued	12

Control Systems Overview continued	13

System setup, configuration and device commissioning	14

User Interface Reference .......................................................................................................................  32

Troubleshooting	44

## Introduction

DACS (Dialight Architecture for Control System) is an enterprise class industrial lighting control system with many advanced features and capabilities.

The system consists of lighting devices and sensors which are connected to a local gateway device via a wired or wireless network.

Multiple gateways are in turn connected to a centralized server which generates the control and user interface functionality.

## Technical Specifications

| Certification | UL 60950-1 CAN/CSA-C22.2 No. 60950-1 EN 60950-1 JEC 60950-1 FCC CFR ICES – 003 EN 55022 EN 55024 VCCI V-3, V- 4 KN – 22 KN – 24 CNS 13438 CISPR 22 |
| --- | --- |
| DC Power Voltage | 12 – 19VDC, 65 W |
| Operating Temperature For Indoor Use Only | NUC Server Operating Temperature: 0 to 50oC |
| Ethernet | 10/100/Gb Ethernet |
| Memory (RAM / SSD) | 8 GB DDR3 / 250 GB mSATA |
| Dimensions | 4.59’’ x 4.41’’ x 1.36’’ |
| Dialight Part # | 9900SLS000100 |
| Manufacturer Part # | D54250WYK |

## System Architecture Overview

- System Architecture Overview

  - Architecture diagram

Figure 1 shows the DACS control system architecture.

  - System Components

    - Enterprise server

At the heart of the DACS system is the enterprise server.

This computer runs software which performs the system-wide control and monitoring functions, plus it serves the web-based user interface applications which are used for system commissioning, configuration and control.

    - Gateway

The DACS gateway is a networking device which connects devices to the enterprise server.

Up to 125 individual devices may be connected to each gateway.

Additionally gateways provide local control for emergency override of schedules, allowing all lights connected to that gateway to be instantly turned on with a single button press.

    - Devices

      - LED High Bay Fixture

LED lighting fixtures are the main device-type which is controlled by DACS.

Adjusting when lights are activated as well as the output dimming level of the fixture is part of the central control functionality offered by the system.

      - WOS Sensor

Dialight’s Wireless Occupancy Sensor is a sensor device which detects motion of human occupants in a particular space and can be configured to activate a group of lights.

WOS sensors may be used to lower operational cost by only turning on lights when they are needed.

Two models of sensor are available; one sensor offers long-range detection while a second model offers a wide-angle of detection.

3.	DLH Sensor

The Daylight Harvesting Sensor is a sensor device which measures the ambient light level in a particular space.

The DACS system can use this information to modulate the dimmer level of the lighting fixtures in the area to minimize power consumption while providing a calibrated and constant illumination level within the space.

DLH sensors are often used in areas that contain sky-lighting as the collected sunlight can be used to offset the output level of the powered lighting fixtures, thereby reducing operational cost.

## Control Systems Overview

- Control System Concepts Overview

- Introduction

There are a few central concepts used repeatedly throughout DACS which are helpful to understanding how the system operated. This section aims to provide a brief overview of these concepts.

- Groups

In DACS the term “Group” refers to a collection of devices. This may be a combination of lights and sensors. Devices, that are part of a group, are affected by control events set for that group.

Additionally, devices may be members of more than one group at a time. This allows for maximum flexibility for creating zones of coverage and control.

  - Control Events

A control event is a command or action which acts upon a group of devices. This may consist of a dimming level sent to a group of lights to set the current light level.

  - Schedules

At the most basic level, a Schedule is a collection of control events. These are most typically used to turn the lights on in an area at a particular time during the day and to turn the lights off at the end of the day.

Schedules are also used to specify when a particular group will react to Occupancy Sensing or Daylight Harvesting sensors.

Schedules are created, defined and uniquely named from within the DACS user interface application. They contain a collection of control events and are configured to operate during selected days of the week. Once a schedule has been created it may be added to a particular Group.

## Control Systems Overview continued

Example:

- A system installer could create a Schedule named “Weekday Schedule” which contains an event to set the dimmer level to 80% at 7:00am each morning and a second event to set the dimmer level to 0% (Off) at 6:00pm each evening.

- This Schedule could then be added to Groups named “South Floor” and “North Floor” and the devices in these two groups would operate on the “Weekday Schedule.”

  - Alerts

Alerts are used to signal error or warning conditions within the DACS system. DACS provides a rules engine which allows users to configure the system to watch for particular Alert conditions.

- Alerts are visible on the Alert page of the DACS user interface application.

- A typical Alert would be set to signal if a device has stopped communicating with the control system.

  - Notifications

A Notification is an automated method to report an alert via sending a message to a User via some external means. Notifications announce an Alert directly to the system operator without the need to view the DACS user interface application.

Supported Notification types include:

- Email

- SMS Text Message

- Twitter Notification

## Control Systems Overview continued

  - Gateway operation modes

    - DACS mode: The gateway acts as a part of the DACS structure.

    - Stand-alone mode: The gateways acts independently, not part of the DACS structure. See Highbay Gateway User Manual for operating instructions.

  - User Accounts

Users of the DACS system are given individual logon User Accounts. These consist of a user name, password and additional information used to send notifications such as an email address and mobile phone number.

  - Automated Demand Response

Automated Demand Response (ADR) is an electric utility-driven communications protocol which enables utility companies to request enrolled customers to reduce their overall facilities power consumption during times of peak demand. This automated load-shedding is helpful to extend the capabilities of the existing power distribution grid infrastructure and results in significant rebates and cost savings for the ADR enabled customer.

DACS supports the industry leading ADR specifications OpenADR V1.0 as well as V2.0.

## System setup, configuration and device commissioning

- System setup, configuration and device commissioning

  - System Setup Overview: System Installation and Commissioning Steps

    - Install lights

    - Install sensors

    - Gateway Installation

    - Install Enterprise Server

    - Commissioning and setup

  - Light Installation

    - Reference light installation guide for Wireless or Dali

  - Sensor Installation

    - Reference sensor manual for installing WOS or DLH sensors

  - Gateway Installation

    - Reference Highbay Gateway manual for physical installation, mounting and installation requirements.

    - Configure Gateway name following instructions in Highbay Gateway manual

    - Configure wired Ethernet IP address following instructions in Highbay Gateway manual

    - Configure Wi-Fi following instructions in Highbay Gateway manual

    - Configure server address following instructions in Highbay Gateway manual

## System setup, configuration and device commissioning: Continued

  - Enterprise Server Installation

1. Power DACS server on with a keyboard, monitor and Ethernet cable connected
2. Enter username (Dialight) and password (password) when prom-pted
3. Type in the following (the default password is “password”): sudo service dacs status
4. There should be 6 processes running
5. You can find the address of the server by typing in the following: echo $IP
6. Put the IP address into the URL line in a browser running on another computer on the same network and hit “Enter”
7. You should now see the DACS login screen

Change the DACS server from using a DHCP address to a static address.

To change the IP for a DACS server to use a static address: 
1. Log in (as user Dialight) 
2. Open the interfaces file:
    `sudo vim /etc/network/interfaces`
3. Find the section for em1 (on, or about, line 9), it will start with: auto em1
5. Delete all the lines BELOW the "auto em1" line (move cursor to appropriate line, then type `dd`),
6. Using data provided to you by your network administrator (for 'aaa', 'bbb', 'ccc', 'ddd' and 'eee'), add in the following 4 lines at the end of the file by entering 'edit' mode (by typing an `i`) :

iface em1 inet static
address aaa.bbb.ccc.ddd
netmask 255.255.255.0
gateway aaa.bbb.ccc.eee
  
7. Type the `Esc` key (to exit edit mode),
8. Type `:wq`, this will write (save) the file, and exit (quit) the editor
9. Now you can reboot the DACS server (this may ask you to re-enter the password):
  `sudo reboot`

## System setup, configuration and device commissioning: Continued

  - DACS User Interface Web Application Login

    - Launching the UI

      - Enter the enterprise server IP address into the URL line in a browser on the same network and hit “Enter”

      - Enter default Username: admin

      - Enter default password: password

      - Select Login

## System setup, configuration and device commissioning: Continued

      - You are now at the homepage

## System setup, configuration and device commissioning: Continued

    - Account setup and login

      - Go to homepage

      - Select system configuration

      - Select Users Icon

        - Select Create User Icon

          - Enter First Name

          - Enter Last Name

          - Enter Email address

          - Create a username

          - Create a password

          - Retype password

          - Select save

      - New user account is now ready to use

  - Gateway discovery

      - How to Discover a Gateway on the DACS system

    - Power up gateway

    - Ensure gateway is plugged into your Ethernet Network

    - Verify IP for DACS gateway on display screen

    - Enter the Gateway IP address into the URL line in a browser on the same network and hit “Enter”

    - Select Configure

## System setup, configuration and device commissioning: Continued

    - Select desired Gateway Mode

      - DACS

      - Stand-alone

    - Enter Enterprise Server IP

    - Enter Enterprise Server Port

    - Select Desired IP Configuration

      - DHCP

      - Static

        - Enter Ethernet IP address

## System setup, configuration and device commissioning: Continued

Enter Ethernet Netmask

        - Enter Ethernet Gateway address

    - Select Save

    - Enter the Enterprise Server IP address into the URL line in a browser on the same network and press  the “Enter” key.

    - Enter a valid username and password to login

    - Select System Configuration

    - Select Gateways Icon

    - Look for your gateway IP address in the list of gateways

- How to check and change gateway settings

    - Login to gateway

    - Select System Configuration

    - Select Gateways Icon

    - Select Manage Icon

## System setup, configuration and device commissioning: Continued

    - Configure a Gateway

      - Add or change Gateway Name

      - Add or change Description

      - Select Discovery Mode to discover devices

      - Identify a device connected to gateway

      - Delete a device connected to gateway

      - Ethernet Setting’s (In accordance to user’s network definition)

        - Select DHCP or Static IP Configuration

        - Add or Change IP Address

        - Add or Change Subnet Mask

        - Add or Change Gateway

      - Wi-Fi Settings

        - Add or Change SSID

        - Change Channel

        - Add or Change WPA Passphrase

      - Select Save

## System setup, configuration and device commissioning: Continued

  - Device Discovery

    - Device discovery process

      - Select System Configuration Icon

      - Select Gateways Icon

      - Select Manage Button

      - Select Discovery Mode

        - Turn off Discovery mode by pushing Discovery Mode button

      - Select System Configuration Icon

      - Select Devices Icon

      - A list of the discovered devices is shown on this page

    - Troubleshooting devices that do not discover

      - Ensure that device is getting correct supply voltage

      - Power cycle device

## System setup, configuration and device commissioning: Continued

    - Device setup

      - Identify device

        - Select System Configuration

        - Select Devices Icon

        - Select Identify Button

        - Stop the identify process by pushing the identify button again

      - Device naming

        - Select System Configuration

        - Select Devices Icon

        - Select Manage

          - Add or change device name

          - Select Save

  - Creating and Managing Groups

(see User Interface Reference section for Groups pg.37 for screenshots)

    - The next step in system setup is to create groups of devices such that they may be controlled in congress. Groups consist of a collection of devices and may include any combination of lights and sensors -- up to 125 devices.

    - From the main page, select System Configuration, then select Groups

    - To create a new schedule, click the “Create Group” button on the top right

    - This will create a pop up screen requiring the user to enter a group Name and Description

    - Click the “Save” button to create the group.

    - The new group should now be listed in the Manage Groups list with 0 Devices and no assigned schedules

    - Click “Manage” to edit the group parameter. This will open the Configure Group screen

    - In the new screen, verify that the Name and Description fields match the intended group

    - Next, add the associated devices. The devices will be part of this group. Click the Associate Devices button

    - An Add/Remove Devices pane will appear with all Available Devices on the right of the screen, and all Selected Devices on the left of the screen.

    - Select the desired devices from the Available Devices group. (Ctrl + click to select multiple devices at once)

## System setup, configuration and device commissioning: Continued

    - The click the Left arrow () to move the desired devices into the Selected Devices list.

    - Devices can be removed from the Selected Devices list, by selecting them and then clicking the right arrow ()

    - Once satisfied, click the “Save” button to save the associated devices

    - The devices should now be listed in the Configure Group page

    - Next, select a schedule that the group will follow. This located near the Associated Schedules title

    - The Associated Schedules button shows the numbers of existing and available schedules. If NO schedules exist or have been created, follow part j:Creating and Managing Schedules

    - If schedules do exist, click the Associated Schedule button

    - An Add/Remove Schedules pane will appear with all Available Schedules on the right of the screen, and all Selected Schedules on the left of the screen

    - Select the desired schedules from the Available Schedules group.

    - The click the Left arrow () to move the desired schedules into the Selected Schedules list.

    - Schedules can be removed from the Selected Schedules list, by selecting them and then clicking the right arrow ()

    - NOTE: It is the user’s responsibility to make sure that multiple schedules do not contradict each other!

    - Once satisfied, click the “Save” button to save the associated schedules

    - The schedules should now be listed in the Configure Group page

    - Scroll down slightly on the Configure Group page. The schedule is graphically displayed in the Dimming Schedule and Sensor Schedule graphs.

    - Scroll back up to the top. If the user schedule contains any WOS or DLH event, they can be configured by clicking the “WOS Stepdown Schedule” button or “Daylight Harvesting” button, respectively.

    - Click the WOS Stepdown Schedule button. A pane with 3 steps will appear. For each step select a power level and duration. When the WOS is triggered, the light will follow this schedule for the desired amount of time. Click “Save” to save the WOS event.

## System setup, configuration and device commissioning: Continued

    - Click the Daylight Harvesting Schedule button. A pane with the DLH parameters will appear. Use the slider to set the current power level during the lights in the group (OFF to 100%), then use the Mode dropdown menu to select the multi-sensor operation (Minimum, Average, or Maximum). If only 1 DLH sensor is in the group, all 3 modes will act the same. The third field shows the current DLH reading. This is the light level the DLH event will maintain by dimming or brightening the light. When the schedule enters the DLH event (as seen in the Sensor schedule graph), the light will react to the ambient light level to maintain a constant light level in the facility.

Click “Save” to save the DLH parameters. Note: As recommended in the DLH User Manual, setting up the DLH event is easiest at night.

    - A pop up will appear indicating that the DLH parameters may contradict the Dimming schedule (previously set by the schedule). Click “save” again if this is not an issue. Once the DLH event is over, the light will return to its scheduled dim level.

    - Finally, once satisfied with all prior steps, click “Save” on the bottom of the Configure Group page. This will return the user to the Manage Groups list.

    - The new group should now list the number of associated groups and have the “Schedules Assigned” column checked ()

  - Creating and Managing Schedules

(see User Interface Reference section for Groups pg.38 for screenshots)

    - A schedule is a series of command events that run over time to control the lighting system. These events are assigned a control operation along with a time to be executed and a collection of these events creates a full control program for the system.

    - From the main page, select System Configuration, then select Schedules

    - To create a new schedule, click the “Create Schedule” button on the top right

    - This will create a pop up screen that allows the user to set up a new schedule

    - Here the user can name the schedule, select operation days, events and light levels.

## System setup, configuration and device commissioning: Continued

    - “Days to Affect” field lets the user set up the days of the week the schedule is in effect

    - “Events” field lets the user set up various events (Light level, DLH, and WOS) during various times each day

      - To create a new event click the “ + Add” button next the “Events” title

      - First select the time the event is in effect (hour then minute)

      - Then select the type of event – Light level, Occupancy or Daylight Harvesting

      - Then select the “Value” of the event

        - If Light Level type was selected, then the user can set the lumens percentage of the light ranging from Off to 100% @ 10% intervals

        - If Occupancy Sensor type was selected, then the user can set the WOS operation as “ON” or “OFF”. Note: Create a separate ON and OFF event if the occupancy sensor is required to work during certain time ranges

        - If Daylight Harvesting type was selected, then the user can set the DLH operation as “ON” or “OFF”. Note: Create a separate ON and OFF event if the DLH sensor is required to work during certain time ranges

      - Once satisfied, click the “Save” button to save the new event.

    - To change or fix existing events, click the “Manage” button of the desired event.

    - To delete an event, click the “Delete” button of the desired event. A pop up will appear confirming the user’s deletion.

    - As events are set, graphs will appear on the right of the Schedule pane reflecting the event parameters.

    - Scroll to the bottom of the Scheduling pane. Once satisfied, click the “Save” button, to save the newly created schedule

    - To change or fix existing Schedules, click the “Manage” button of the desired schedule.

    - To delete a Schedule, click the “Delete” button of the desired schedule. A pop up will appear confirming the user’s deletion.

    - Schedules can be associated with new or existing Groups.

## System setup, configuration and device commissioning: Continued

  - Daylight Harvesting Setup

    - Go to System Configurations, then Gateway

    - Select Manage on the Gateway that the DLH sensor should belong to

    - Once selected a pop up window with the Gateway’s information will appear

    - Turn on Gateway discovery by pressing the Discovery Mode button

    - Then simply wait for the desired DLH sensor to join the network

    - Turn off discovery by pressing the Discovery Mode button again

    - Exit the Gateway management screen by pressing the “x” on the top right hand corner of the pop up

    - Return to System Configurations to set up a new Schedule with the desired DLH sensor or to add the DLH sensor to a new or existing Group.

    - Optionally, check that the DLH sensor is listed under the Devices menu

  - Occupancy Sensor Setup

    - Go to System Configurations, then Gateway

    - Select Manage on the Gateway that the WOS sensor should belong to

    - Once selected a pop up window with the Gateway’s information will appear

    - Turn on Gateway discovery by pressing the Discovery Mode button

    - Then simply wait for the desired WOS sensor to join the network

    - Turn off discovery by pressing the Discovery Mode button again

    - Exit the Gateway management screen by pressing the “x” on the top right hand corner of the pop up

    - Return to System Configurations to set up a new Schedule with the desired WOS sensor or to add the WOS sensor to a new or existing Group.

    - Optionally, check that the WOS sensor is listed under the Devices menu

## System setup, configuration and device commissioning: Continued

- System Operation

  - System Health Monitoring

    - There are many ways to gauge the connectivity of the DACS system.

    - In the Main page or Under System configuration, click “Device”.

    - The Manage Devices page displays all connected devices and their connection status. Lights that are connected have a  in the Is Connected column. The user can verify that all desired units are connected. (Verify that units that are not connected are simply unplugged).

    - The user can also identify each unit by clicking the “Identify” button. The corresponding unit will begin to blink at a moderate pace. Blinking can be stopped by clicking the “Identify” button again. The light will return to its scheduled dim level.

    - User can click “Manage” in the light’s row to verify the light’s parameters: RF Parent, Software Version, UID, Power, Number of groups, RF strength, etc. The user can manually move the dim level slider to validate responsiveness of the light.

  - Group Manual Override

    - Group Override allows the user to manually control the dimming of lights in groups independent of their selected schedules. The user can effectively, temporarily, disable schedules without deleting groups or schedules.

    - From the main page go to Group Control

    - In Group Control there will be a list of individual groups defined by the user and All Devices “super-group”.

    - All Devices allows the user to take full control off all the lights on the DACS network. While individual groups only control that single group

    - Click the green Override button in the Action column. Once clicked, the user gets control of the dimming slider. The user can set the slider to the desired dim level of the group (or all lights)

## System setup, configuration and device commissioning: Continued

    - To return to the scheduled operation of the group, click the red Resume button in the Action column (was Override). The group (or all groups for All Devices) will return to its scheduled dim level. This will be reflected by the dim slider.

    - Lights and groups will remain in override mode until the resume button is pressed

  - Changing Dimming Schedules and Sensor Actions

    - Often the user may want to adjust a schedule, without creating a new one and associating it with groups. The user can simply change events in the schedule, and all groups following that schedule will respond accordingly.

    - As described is Section III Part J step xii, schedules can be managed by Selecting “Manage” near the desired schedule

    - In the Configure Schedule panel, Events can be deleted or managed to change their parameters. New events can be added by clicking the “+Add” button and following step vii in Part J of Section III

    - Note: Changed events will only take place when the event time has been reached. Therefore if the current event (suppose light level) is being changed at 2PM, but occurred at 1PM, then the system will wait until 1PM the next day to update the event.

    - Note: If all events are deleted, the light will maintain its last dimmer value

    - Note: Daylight Harvesting and Occupancy Sensor events do not automatically turn off when deleted. The user must turn off those events by creating an OFF event at the nearest time. Once the OFF event is triggered, the user can choose to delete the event.

    - Note: In the DACS system, event are only updated and acted upon, when the event time is reached. Therefore it is best to set new events to occur after the “current” time. (If the user is setting up events at 2PM, then those events should be set to trigger after 2PM, else they will be acted upon during the next day).

## System setup, configuration and device commissioning: Continued

- Demand Response Setup and Operation

ADR Installation

The DACS system uses the ISY device from Universal Devices to communicate with the utility’s VTN server for OpenADR signals.  The ISY device should be installed on the same network subnet as the DACS system for automatic configuration between DACS and ISY via UPnP.  If your network configuration does not allow you to install the ISY device on the same subnet, please contact Dialight support for help updating the DACS configuration to specify the ISY’s IP address.

Next the ISY device needs to be configured to communicate with the VTN server.  Please use the setup instructions on the vendor’s site at http://wiki.universal-devices.com/index.php?title=Main_Page#OpenADR along with the VTN connection details from your utility company.

of a future event by clicking on the Manage button for that event.  An ADR Event Details dialog will open with additional information about the event and the option to change

## System setup, configuration and device commissioning: Continued

ADR Operation

ADR settings in DACS are configured by going to the ADR Management page from the DACS home screen.  The top section of the ADR Management screen shows you the current status of ADR signals, the connection status between DACS and the ISY device, and your current system power consumption.  The Event Opt-in Override button will toggle the opt-in setting for the currently active ADR event.

The Upcoming Events section lists all of the ADR events that the system has received from the utility’s VTN via the ISY device.  Past events can be hidden by clicking the Hide past events checkbox.  All ADR events are set to opt-in by default, but you may opt-out

the Opt-in setting by clicking the checkbox at the top of the dialog and clicking the Save button.  Note that the Opt-in checkbox can only be changed for future events.

The Profile section allows you to configure how the DACS system will behave during an ADR event.  All of the user defined groups of the system will be listed and available for configuration.  ADR events will specify a signal level for the event that correspond to the Stage levels in the Profile section.  In general, higher signals correspond to higher reduction requests, but the meaning of a signal and your expected energy use is defined by your specific utility’s ADR program.  To enable a group for participation in an ADR event, click the checkbox for each Stage level the group should participate in.  Then set the group’s light level by clicking the Override button and adjusting the slider.  As you adjust the slider, the group’s power usage will update as will the total power usage for that stage.  Once you are happy with both the light level and the power usage values, click the Resume button to save the setting for that group at that stage level.  Repeat this process to configure all of the groups and stages that you need to for your ADR program.

When an ADR event becomes active, all participating groups for the event Stage level will be commanded to their defined levels.  Note that an ADR event has priority over normal schedules and daylight harvesting settings.  However, manual override and emergency override commands will take precedence over an active ADR event.  Also, you may opt-in or out of an active ADR event by clicking the Event Opt-in Override button in the top section of the ADR Management screen.

- User Interface Reference

Supported Browsers

The suggested browser to use for the DACS system is Google Chrome v. 42 or greater. DACS is also supported on Firefox v.40 or greater.

Login Screen

This is the first screen you will see when trying to access the DACS system. Each user may have a different Username and Password depending on admin requirements. If a password is forgotten, a user can click the Forgot Password link to the right of the Login button which will lead to an email-based retrieval screen.

Main Screen

The main screen gives the user access to all of the features and controls that the DACS system offers. Each sub-menu will direct user to a different feature/control page. The menu bar at the top of the screen also offers quick navigation options as well as an emergency override feature and a real-time clock. Please see below for a detailed description of each sub-menu

The Emergency Override button will automatically bring all lights to 100% ON when pressed.  The button will flash when it is active, and will only turn off when pressed again. The lights will revert to previous dim state/ schedule after Emergency Override is turned off.

The Home button will bring the user back to the main screen regardless of what page they are on. Use this to quickly navigate back to the home screen

The Alerts button will bring the user to the alerts page. Use this to quickly navigate to the Alerts page to view/acknowledge alerts

The ADR button will bring the user to the ADR management page. Use this to view and manage ADR events

The Options button will allow the user to log out after they are finished using the system. You can also use this option to find out more about your DACS system

Menu Options

System Configuration – This sub menu will allow you to customize all aspects of your DACS system. This includes adding/removing gateways, lights, and sensors. You can also modify Schedules, Groups, Users, and Alerts

Devices – This sub menu will allow you to view all devices currently connected to your system. You can also view in-depth information about each light/sensor as well as identify each light individually

Alerts – This sub menu will allow you to view and manage all current alerts with the system

Reporting – This sub menu will allow you to print power reports for specific light groups or all connected lights

Group Control – This sub menu will allow you to control your lights outside of schedules. You can dim individual groups or all devices connected to your DACS system

ADR Management – This sub menu will let you view/modify your current ADR events

System Configuration

Clicking the system configuration menu option on the main screen will bring you to a sub menu with several options. See below for detailed description of each.

Gateways – manage the gateways currently connected to the system and add new gateways

Devices – manage all devices currently connected to the system

Groups – Modify/create groups and associate the groups with lights/schedules

Schedules – Create schedules

Users – Add/Manage user accounts

Alerts and Notifications – Create/Modify alerts and notifications

Gateways

Clicking the gateway menu will open the manage gateways page. This page allows you to see all gateways currently connected to the DACS system. You can see IP addresses assigned to each gateway as well as the number of devices currently connected. More gateways can easily be added on this page. After a gateway is connected, you can manage it by selecting the Manage button which will bring up the following screen:

This pop-up window will allow you to configure the following parameters:

- Name

- Network Settings

- Wifi Settings

- Connected devices

Please refer to the section on Connecting Devices for a more in-depth guide

Devices

Clicking the devices menu will open up the Manage Devices page. This page allows you to view/manage all devices currently connected to your DACS system. You will be able to see which devices are connected as well as information about each device. You can click the Manage button which will open the following screen:

This screen gives you a wealth of information about the selected device as well as a few changeable features:

- Name (unique name for each device)

- Set dim level for individual lights

- Identify device for easy location management

Groups

Clicking the Groups menu will open up the Manage Groups page. This page allows you to view/manage all groups currently set up on your DACS system. You can create/edit all groups from this screen regardless of which gateway they are connected to. After creating a group, you can manage it by clicking the Manage button which will open a page with several group options. These include:

Name and Description: Give each group a custom name and description for better identification

Manage Sensors: Set your Occupancy sensor Stepdown Schedule and Daylight Harvesting light levels.

NOTE: This can only be used if you have WOS or DLH sensors installed. Refer to respective manuals for more in-depth guide

Associated Devices: view and manage all devices currently in selected group. You can add/delete devices by selecting the Associate Devices button

NOTE: Devices must be associated with a group to interact with schedules/group commands. See configuring groups section for a more in-depth guide

Associate Schedules: view and manage all schedules currently associated with selected group. You can add/delete schedules by selecting the Associate Schedules button. Once a schedule is associated with a group, a visual display of the schedule will appear in the graphing section at the bottom of the page.

NOTE: Schedules must be associated with a group to interact with lights/sensors. See configuring schedules section for a more in-depth guide

Schedules

Clicking the Schedules menu will open up the Manage Schedules page. This page allows you to view/manage all schedules currently set up on your DACS system. You can create/edit all schedules from this screen regardless of which group they are connected to. You can create a new schedule by clicking the Create Schedule button which will open the following page:

This screen allows you to customize a schedule for any situation. You can set events for dimming as well as turning on and off sensors. The schedule will interact with all devices in a specific group once the schedule is associated with said group. Please refer to scheduling section for a more in-depth guide.

Users

Clicking the Users menu will open up the Manage Users page. This page will let you see all user accounts currently configured for the DACS system. This screen will also show you the authorization level for each account. To create a new account, simply click the Create Account button which will open the following screen:

Usernames can be set up with the following custom parameters:

- First and last name

- Email address (used for forgotten password retrieval)

- Username

- Password

- User Role

Alerts and Notifications

Clicking the Alerts and Notifications menu will bring you to the Manage page for all Alerts and Notifications currently set up on the DACS system. These can be custom made for a wide variety of parameters that could occur within the system. Hitting the Create Alert button will open the following page:

Some of the notable features in this screen include:

- Custom event name, description, severity

- Custom alert criteria which can apply to a single light, group of lights, or even a gateway

- Notification recipients

  - Alerts can be sent to any number of recipients over a variety of methods including

    - Twitter

    - Email

    - SMS

NOTE: Alerts can be tailored to custom parameters using the Alerts Rules Engine. Please refer to Alerts section for a more in-depth guide

Devices

Clicking the devices screen on the main page will bring you to the Manage Devices page. This is the same page that can be accessed from the System Configuration menu. Use this page to manage/view all devices currently connected to your DACS system. You can also use this page to:

  - Identify individual lights

  - Rename lights

  - Delete lights

  - Verify light communication

  - Get various information about light

    - RF signal Strength

    - RF parent

    - UID

    - Temp

    - Lumens Output

NOTE: If you are looking to add new devices, you will need to do this using the System Configuration Menu. See section about connecting devices for a more in-depth guide

Alerts

Clicking the Alerts menu on the main page will bring you to the Manage Alerts page. This is different than the Alerts Configuration page which can be accessed from the System Configuration menu. Use this page to view all current active and acknowledged alarms on the system:

  - View in-depth info on each alert  by clicking the Manage button

  - Acknowledge alerts

  - Delete Acknowledged alerts

Reporting

Clicking the Reporting menu on the main page will bring you to the Reporting page. Use this page to print out power reports for various lighting configurations. Select desired group and time period and select the Go button to save a custom report file

Group Control

Clicking the Group Control menu on the main page will bring you to the Group Control page. Use this page to control groups of lights or all current lights connected to the system. To control these groups, you will need to override the schedule set for each group. The schedules will not resume until you click the resume button

NOTE: Groups must be configured before they can be controlled. See Group Configuration section for a more in-depth guide

ADR Management

Clicking the ADR Management menu on the main page will bring you to the ADR Management page. Use this page to view upcoming ADR events, Opt-out of events, and set desired stage profiles.

NOTE: please see ADR Management section for a more in-depth guide

## Troubleshooting

- Troubleshooting

This section is needs some basic troubleshooting information; things to try, problems that may exist, typical user error. This section may contain whatever we would like to include to make solving problems easier.

REVISION HISTORY

REV	ECO No.	DRN		CKD		APP		QA		CM		 DATE

1.2