# Dialight DACS EtherNet/IP Adapter

User Reference Manual

# Lighting System

The DACS Lighting System Server provides an automated interface, through which a user can control and monitor all the connected devices in a building-wide light control system.

## Overview

A DACS Lighting system consists of multiple ‘nodes’ in a network:

- DACS Server: The DACS Server is the ‘root’ node of the system.  It controls and monitors all other nodes on the network.

- Gateway: Gateways interact directly with the DACS Server.  They provide a network junction through which groups of lights and sensors can connect.

- Devices: “Devices” consist of any lights or sensors which are part of the lighting ecosystem.  Devices participate in the network by connecting to a gateway.

In addition to these physical nodes, the DACS Server provides a number of virtual ‘objects’ used for grouping, scheduling, and other diagnostic purposes:

- Groups: represent a logical ‘grouping’ of multiple devices.

- Schedules: contain a list of logical rules, used for controlling the behavior of the lighting system.

- Alerts: contain important diagnostic information intended for the system administrator.

An example of a typical lighting system tree is provided in the following chart:

Note: Every gateway, device, group, schedule and alert provides a unique “UID” string value, with which it can be identified or addressed.

## EtherNet/IP Connectivity

The DACS Server provides EtherNet/IP connectivity, via an Adapter interface running on the server itself.  This EtherNet/IP Adapter acts as a protocol bridge between a PLC (or compatible EtherNet/IP device) and all participating nodes and objects in the Dialight lighting control system.

All devices, gateways, groups, schedules and alerts in the DACS lighting system are modeled as a series of “DACS Objects,” which are uniquely identified by a string UID value.  Each DACS Object provides a set of “DACS Object Properties” with read and/or write access.  It is through the various DACS Object Properties that an EtherNet/IP-enabled controller can interact with nodes and affect behavior on the DACS lighting system.

On the EtherNet/IP side of the bridge; the application defines a set of vendor-specific EtherNet/IP application objects, through which incoming EtherNet/IP requests are translated and forwarded to the DACS server.  Once a response is received from the DACS server, the adapter converts and delivers the response to the requesting device.  These vendor-specific EtherNet/IP Application Objects are described in further detail in this document.

Figure 1- Communication between PLC and DACS server

In addition to the explicit request/response paradigm, an EtherNet/IP-enabled device can monitor the lighting system for changes in state, using a Class 1 I/O connection and reacting to new data.  These changes in state are triggered by “DACS Server Events,” originating from the lighting system.

### DACS Object Properties

The DACS EtherNet/IP Adapter provides a ‘Get/Set’ API, providing read and/or write access to a DACS Object’s individual properties.  The properties available to the target DACS Object depend on the underlying type; gateway, device, sensor, etc.  Some DACS Object types can inherit groups of properties from a common ‘base’ type.

The DACS Server itself provides some ‘root-level’ properties only available by addressing the DACS Server itself, using the reserved UID: “Lighting-System”.

Each property is identified by a unique 16-bit ID.  Each property is reported in its prescribed CIP Data Type.

The full list of properties is defined below, including the parent DACS Object ‘type,’ allowable access, the unique ID, and a brief description.  Some properties require additional ‘argument’ parameters.  They are identified in the “Required Args” column.

| Property ID | Access | Property Name | CIP Data Type | Description | Required Args |
| --- | --- | --- | --- | --- | --- |
| Lighting System |  |  |  |  |  |
| 0x0001 | Get | GATEWAY_LIST_SIZE | UDINT |  |  |
| 0x0002 | Get | GATEWAY_LIST_GET_ELEMENT | STRING | Return the UID of the Gateway at the specified index | Index of the desired element (UDINT) |
| 0x0003 | Get | ALERT_LIST_SIZE | UDINT |  |  |
| 0x0004 | Get | ALERT_LIST_GET_ELEMENT | STRING | Return the UID of the Alert at the specified index | Index (UDINT) |
| 0x0005 | Get | SCHEDULE_LIST_SIZE | UDINT |  |  |
| 0x0006 | Get | SCHEDULE_LIST_GET_ELEMENT | STRING | Return the UID of the Schedule at the specified index | Index (UDINT) |
| 0x0007 | Get | GROUP_LIST_SIZE | UDINT |  |  |
| 0x0008 | Get | GROUP_LIST_GET_ELEMENT | STRING | Return the UID of the Group at the specified index | Index (UDINT) |
| 0x0009 | Get | DEVICE_LIST_SIZE | UDINT |  |  |
| 0x000A | Get | DEVICE_LIST_GET_ELEMENT | STRING | Return the UID of the Device at the specified index | Index (UDINT) |
| 0x000B | Get / Set | EMERGENCY_OVERRIDE | BOOL |  |  |
| 0x000C | Get | SYSTEM_POWER_ CONSUMPTION | UDINT |  |  |
| 0x000D | Get | SYSTEM_SOFTWARE_VERSION | STRING |  |  |
| 0x000E | Set | GROUP_LIST_CREATE_ELEMENT | None* | Create a new Group object. Creation is performed asynchronously, and completion is signaled by the “GROUP_LIST_SIZE Changed” event. Once the signal has been triggered, a client can retrieve the UID of the newly-created object by getting the UID of the last element in the Group list (GROUP_LIST_GET_ELEMENT). |  |
| 0x000F | Set | GROUP_LIST_DELETE_ELEMENT | UINT32 | Delete the Group object located at the given index. | The index of the Group object to delete, as positioned in the GROUP_LIST array. |
| 0x0010 | Set | SCHEDULE_LIST_CREATE_ELEMENT | None* | Create a new Schedule object. *Creation is performed asynchronously, and completion is signaled by the “SCHEDULE_LIST_SIZE Changed” event. Once the signal has been triggered, a client can retrieve the UID of the newly-created object by getting the UID of the last element in the Schedule list (SCHEDULE_LIST_GET_ELEMENT). |  |
| 0x0011 | Set | SCHEDULE_LIST_DELETE_ELEMENT | UINT32 | Delete the Schedule object located at the given index. | The index of the Schedule object to delete, as positioned in the SCHEDULE_LIST array. |
| Device |  |  |  |  |  |
| 0x0100 | Get / Set | NAME | STRING | Friendly name for the device. |  |
| 0x0101 | Get | UID | STRING | Unique identifier |  |
| 0x0102 | Get | MODEL_NAME | STRING | This is a human readable model description |  |
| 0x0103 | Get | MODEL_NUMBER | STRING | This is manufacturers part number for the device |  |
| 0x0104 | Get | MANUFACTURER | STRING | String representation of the product manufacturer |  |
| 0x0105 | Get | DEVICE_TYPE | USINT | Device object subtype (see Appendix A for enumerated list of device sub-types) |  |
| 0x0106 | Get | CONNECTED | BOOL | Is the device currently online |  |
| 0x0107 | Get | FIRMWARE_VERSION | STRING | Software version of the device |  |
| 0x0108 | Get / Set | IDENTIFY | BOOL | Is identify mode currently enabled? |  |
| Basic Light (Inherits: Device) |  |  |  |  |  |
| 0x0200 | Get / Set | LIGHT_LEVEL | USINT | Dimmer level of light |  |
| 0x0201 | Get / Set | OVERRIDE | BOOL | Flag for if the level is currently overridden |  |
| HB Light (Inherits: Device, Basic Light) |  |  |  |  |  |
| 0x0300 | Get | POWER_CONSUMED | UDINT | Watts consumed x 10 |  |
| 0x0301 | Get | LUMENS_OUTPUT | UDINT | light output in lumens |  |
| 0x0302 | Get | TEMPERATURE | INT | Temp in F (signed INT) |  |
| 0x0303 | Get | LAMP_HOURS | UDINT | Total hours of lamp operation |  |
| 0x0304 | Get | RF_STRENGTH | UINT | Number representing signal strength |  |
| 0x0305 | Get | RF_PARENT | STRING | UID of network parent |  |
| Basic Sensor (Inherits: Device) |  |  |  |  |  |
| 0x0400 | Get | SENSOR_SUB_TYPE | USINT | Sensor sub-type (see Appendix A for enumerated list of sensor sub-types) |  |
| WOS Sensor (Inherits: Device, Basic Sensor) |  |  |  |  |  |
| 0x0450 | Get | MOTION_SENSED | BOOL | True == Motion Sensed |  |
| 0x0451 | Get | BATT_VOLTAGE | UINT | Voltage x10 |  |
| WDLH Sensor (Inherits: Device, Basic Sensor) |  |  |  |  |  |
| 0x0500 | Get | LUX | UINT | Light level reading in LUX |  |
| Gateway (Inherits: Device) |  |  |  |  |  |
| 0x0600 | Get | JN_FIRMWARE_ VERSION | STRING | Firmware version of JN co-processor |  |
| 0x0601 | Get | SERVER_IP_ADDR | STRING | IP address as a string |  |
| 0x0602 | Get | SERVER_PORT | UINT | port addr |  |
| 0x0603 | Get | ETHERNET_TYPE | STRING | DHCP or Static |  |
| 0x0604 | Get | GATEWAY_IP_ADDR | STRING | Ethernet IP address of the gateway itself |  |
| 0x0605 | Get | GATEWAY_NETMASK | STRING | Network mask of the gateway |  |
| 0x0606 | Get | GATEWAY_ROUTER | STRING | Ethernet IP gateway address setting for the gateway |  |
| 0x0607 | Get | WIFI_SSID | STRING | SSID for the onboard Wi-Fi host |  |
| 0x0608 | Get | WIFI_CHANNEL | UINT | Wi-Fi channel to use for hostapd |  |
| 0x0609 | Get / Set | DISCOVER | BOOL | Is discovery mode enabled |  |
| 0x060A | Get | GWY_DEVICE_LIST_ SIZE | UDINT | Number of elements in gateway device list |  |
| 0x060B | Get | GWY_DEVICE_LIST_ GET_ELEMENT | STRING | Get device UID at index | Index (UDINT) |
| Group |  |  |  |  |  |
| 0x0700 | Get / Set | GRP_NAME | STRING | Friendly name for the group |  |
| 0x0701 | Get / Set | GRP_DESCRIPTION | STRING | User defined description for the group |  |
| 0x0702 | Get | GRP_POWER_CONSUMED | UDINT | Total power for all devices in the group |  |
| 0x0703 | Get / Set | GRP_LIGHT_LEVEL | USINT | Dimmer level for the group |  |
| 0x0704 | Get / Set | GRP_OVERRIDE | BOOL | Flag to command group manual override |  |
| 0x0705 | Get | GRP_DEVICE_LIST_ SIZE | UDINT | Get number of elements in group device list |  |
| 0x0706 | Get | GRP_DEVICE_LIST_ GET_ELEMENT | STRING | Get device UID at index | Index (UDINT) |
| 0x0707 | Set | GRP_DEVICE_LIST_ ADD_ELEMENT | STRING | Add device to group | The UID of the device to add. (STRING) |
| 0x0708 | Set | GRP_DEVICE_LIST_ REMOVE_ELEMENT | STRING | Remove device from group | The UID of the device to remove. (STRING) |
| 0x0709 | Get | GRP_SCHED_LIST_ SIZE | UDINT | Get number of elements in group schedule list |  |
| 0x070A | Get | GRP_SCHED_LIST_ GET_ELEMENT | STRING | Get schedule UID at index | Index (UDINT) |
| 0x070B | Set | GRP_SCHED_LIST_ ADD_ELEMENT | STRING | Add Schedule to group | The UID of the device to add. (STRING) |
| 0x070C | Set | GRP_SCHED_LIST_REMOVE_ELEMENT | STRING | Remove Schedule from group | The UID of the device to remove. (STRING) |
| 0x070D | Get / Set | GRP_WOS_ENABLED | BOOL | Flag for if WOS is currently enabled |  |
| 0x070E | Get / Set | GRP_WDLH_ENABLED | BOOL | Flag for if WDLH is currently enabled |  |
| 0x070F | Get / Set | GRP_TARGET_LUX | UINT | Target lux value for DLH to adjust to |  |
| 0x0710 | Get | GRP_MEASURED_ LUX | UINT | Current measured lux for the group |  |
| 0x0711 | Get / Set | GRP_WDLH_MODE | USINT | Current WDLH mode (See Appendix A for enumerated list of modes.) |  |
| 0x0712 | Get | GRP_STEPDOWN_LIST_SIZE | UINT32 |  |  |
| 0x0713 | Get | GRP_STEPDOWN_LIST_GET_ELEMENT | STRUCT of STEPDOWN_ELEMENT | Get stepdown schedule item at index. | Index (UINT32) |
|  |  | DURATION | UINT8 |  |  |
|  |  | LIGHT_LEVEL | UINT8 |  |  |
| 0x0714 | Set | GRP_STEPDOWN_LIST_ADD_ELEMENT | STRUCT of STEPDOWN_ELEMENT | Add stepdown schedule item to end of current list. |  |
|  |  | DURATION | UINT8 |  |  |
|  |  | LIGHT_LEVEL | UINT8 |  |  |
| 0x0715 | Set | GRP_STEPDOWN_LIST_REMOVE_ELEMENT |  | Remove stepdown schedule item from index. | Index (UINT32) |
| Schedule |  |  |  |  |  |
| 0x0800 | Get | SCH_NAME | STRING | Friendly name for the schedule |  |
| 0x0801 | Get | SCH_DESCRIPTION | STRING | User defined description for the schedule |  |
| 0x0802 | Get | SCH_DOWEEK | USINT | Days of the week the schedule should run (Note: follows the Unix cron format: both bit 0 and 7 denote Sunday, bit 1-6 denote Mon-Sat). |  |
| 0x0803 | Get | SCH_EVENT_LIST_ SIZE | UDINT | Number of events in the schedule |  |
| 0x0804 | Get | SCH_EVENT_LIST_ GET_ELEMENT | STRUCT of EVENT_DATA | Event configuration structure | Index (UDINT) |
|  |  | EVENT_ID | UDINT |  |  |
|  |  | EVENT_TIME_SEC | USINT |  |  |
|  |  | EVENT_TIME_MIN | USINT |  |  |
|  |  | EVENT_TIME_HOUR | USINT |  |  |
|  |  | EVENT_PARAM | UINT |  |  |
|  |  | EVENT_VALUE | USINT |  |  |
| 0x0805 | Set | SCH_EVENT_LIST_ADD_ELEMENT |  | Add event to the current schedule. * The EVENT_ID value is ignored. The server will populate this value. |  |
|  |  | EVENT_ID | UINT32 |  |  |
|  |  | EVENT_TIME_SEC | UINT8 |  |  |
|  |  | EVENT_TIME_MIN | UINT8 |  |  |
|  |  | EVENT_TIME_HOUR | UINT8 |  |  |
|  |  | EVENT_PARAM | UINT16 |  |  |
|  |  | EVENT_VALUE | UINT8 |  |  |
| 0x0806 | Set | SCH_EVENT_LIST_REMOVE_ELEMENT |  | Remove event from index. | Index (UINT32) |
| Alerts |  |  |  |  |  |
| 0x1000 | Get | ALERT_EVENT_UID | STRING | Event UID that triggered the event |  |
| 0x1001 | Get | ALERT_UID | STRING | Unique identifier for the alert itself |  |
| 0x1002 | Get | ALERT_TYPE | USINT | The severity of the Alert (see Appendix A for enumerated list of alert types) |  |
| 0x1003 | Get | ALERT_STRING | STRING | Information string about the alert |  |
| 0x1004 | Get / Set | ALERT_STATE | USINT | The state of the alert (see Appendix A for enumerated list of alert types) |  |
| 0x1005 | Get | ALERT_TIMESTAMP | UDINT | Unix timestamp of when the alert occurred |  |
| 0x1006 | Get | ALERT_DEVICE_UID | STRING | Device UID that caused alert |  |

### DACS Server Events

In some cases it may not be efficient to continually ‘poll’ a desired property, to detect changes in state.  For these cases, the DACS Server provides a simple “Event” system, to alert controllers of changes in the state of the system.

Each event is identified by a unique, 8-bit ID number.  The complete list of possible DACS Server “Events” is defined below, accompanied with a brief description.

| Event ID | Event Name | Description |
| --- | --- | --- |
| 1 | GATEWAY_LIST_SIZE Changed | Indicates a change in the value of the Lighting System’s GATEWAY_LIST_SIZE attribute |
| 2 | ALERT_LIST_SIZE Changed | Indicates a change in the value of the Lighting System’s ALERT _LIST_SIZE attribute |
| 3 | SCHEDULE_LIST_SIZE Changed | Indicates a change in the value of the Lighting System’s SCHEDULE _LIST_SIZE attribute |
| 4 | GROUP_LIST_SIZE Changed | Indicates a change in the value of the Lighting System’s GROUP _LIST_SIZE attribute |
| 5 | DEVICE_LIST_SIZE Changed | Indicates a change in the value of the Lighting System’s DEVICE _LIST_SIZE attribute |
| 6 | EMERGENCY_OVERRIDE Changed | Indicates a change in the value of the Lighting System’s EMERGENCY_OVERRIDE attribute |
| 7 | Motion Sensed | Indicates a sensor device has detected motion. |
| 8 | GWY_DEVICE_LIST_SIZE Changed | Indicates a change in the value of a gateway’s GWY_DEVICE _LIST_SIZE attribute. |
| 9 | GRP_LIGHT_LEVEL Changed | Indicates a change in the value of a group’s GRP_LIGHT_LEVEL attribute. |
| 10 | GRP_OVERRIDE Changed | Indicates a change in the value of a group’s GRP_ OVERRIDE attribute. |
| 11 | GRP_DEVICE_LIST_SIZE Changed | Indicates a change in the value of a gateway’s GRP_DEVICE_LIST_SIZE attribute. |
| 12 | GRP_SCHEDULE_LIST_SIZE Changed | Indicates a change in the value of a gateway’s GRP_ SCHEDULE _LIST_SIZE attribute. |
| 13 | GRP_WOS_ENABLED Changed | Indicates a change in the value of a gateway’s GRP_ WOS_ENABLED attribute. |
| 14 | GRP_WDLH_ENABLED Changed | Indicates a change in the value of a gateway’s GRP_ WDLH_ENABLED attribute. |
| 15 | SCH_EVENT_LIST_SIZE Changed | Indicates a change in the value of a schedule’s SCH_EVENT_LIST_SIZE attribute. |

# EtherNet/IP Application Objects

The DACS EtherNet/IP Adapter provides a set of vendor-specific CIP Application Objects, through which a controller can interact with the DACS Object Properties and DACS Server Events, outlined above.

## “DACS Control” Object

The “DACS Control” object is the CIP object through which all “Get Property” and “Set Property” requests are directed.

### Class Code

The Class ID of the DACS Control object is 100 (hex 0x64).

### Class Attributes

The Adapter provides the following attributes at the “class” level (instance 0):

| Attribute | Access | Name | CIP Data Type | Description |
| --- | --- | --- | --- | --- |
| 0x01 | Get | Revision | UINT | Get the current revision of the class definition. The current revision of the class is 2. |

### Instances

The Adapter provides only a single instance of the DACS Control object: instance 1 (hex: 0x01).

### Instance Services

The “DACS Control” object provides object-specific CIP services, providing a means through which to Get & Set DACS Server properties.  These services are defined below with a brief description.

Service-specific request data is outlined in the following sections.

| Service Code | Service Name | Description |
| --- | --- | --- |
| 0x4B | Get DACS Property | Read the value of the specified DACS Property, from the object with the specified DACS Object UID. |
| 0x4C | Set DACS Property | Write a value to the specified DACS Property, to the object with the specified DACS Object UID. |

#### “Get Property” Request Data

The “Get Property” service accepts a Property ID value and DACS Object UID value, and returns the value of the specified property.  Additionally, some DACS Server Properties require an additional parameter, such as the desired Index of an array.  The request data for a “Get Property” service request is defined below:

| Required? | Name | EIP Data type | Description |
| --- | --- | --- | --- |
| Required | Property ID | UINT | The 16-bit property identifier of the desired property. For the full list of properties, refer to the table of properties, defined above in “DACS Object Properties.” |
| Required | DACS Object UID | STRING | The UID specifying the desired DACS device, gateway, group, schedule or alert being addressed. Note: The Lighting System has a reserved UID string value of “Lighting-System" |
| Conditional | Parameter | <varies> | For some properties, an additional parameter may be required. These properties are identified in the “DACS Object Properties” table, above, in the “Additional Request Args” column. |

##### Example

An example “Get Property” service request is outlined below.  This example retrieves the current “System Software Version,” from the DACS Server Lighting System.

| Service Code |  | 75 (hex: 0x4B) |  |  |
| --- | --- | --- | --- | --- |
| Class ID |  | 100 (hex: 0x64) |  |  |
| Instance Number |  | 1 (hex: 0x01) |  |  |
| Request Data (Length: 19 bytes) |  |  |  |  |
| Name | Property ID |  | Target DACS Object UID | Parameter |
| Raw Data | 0D 00 |  | 0F 00 4C 69 67 68 74 69 6E 67 2D 53 79 73 74 65 6D | [N/A] |
| Value | [UINT] 13 (0x000D) (‘SYSTEM_ SOFTWARE_ VERSION’) |  | [STRING] ‘Lighting-System’ | [N/A] |

Note: the length of the request data will fluctuate, with variable-length String values.

#### Set Property

The “Set Property” service accepts a Property ID value and DACS Object UID value, as well as the new value to assign to the property.  The request data for a “Set Property” service request is defined below:

| Required? | Name | EIP Data type | Description |
| --- | --- | --- | --- |
| Required | Property ID | UINT | The 16-bit property identifier of the desired property. For the full list of properties, refer to the table of properties, defined above in “DACS Object Properties.” |
| Required | DACS Object UID | STRING | The UID specifying the desired DACS device, gateway, group, schedule or alert being addressed. Note: The Lighting System has a reserved UID string value of “Lighting-System" |
| Required | Value | <varies> | The new value to assign to the target property. Value must match the data type of the property, as defined in the above table “DACS Object Properties.” |

##### Example

An example “Set Property” service request is outlined below.  This example assigns the Light Level of a light named “MyExampleLight” to 100% (hex 0xFF).

| Service Code |  | 76 (hex: 0x4C) |  |  |
| --- | --- | --- | --- | --- |
| Class ID |  | 100 (hex: 0x64) |  |  |
| Instance Number |  | 1 (hex: 0x01) |  |  |
| Request Data (Length: 19 bytes) |  |  |  |  |
| Name | Property ID |  | Target DACS Object UID | Value |
| Raw Data | 00 02 |  | 0E 00 4D 79 45 78 61 6D 70 6C 65 4C 69 67 68 74 | FF |
| Value | [UINT] 512 (0x0200) (‘LIGHT_LEVEL’) |  | [STRING] ‘MyExampleLight’ | [USINT] 255 (0xFF) (100%) |

Note: the length of the request data will fluctuate, with variable-length String values.

## “DACS Event History” Object

The “DACS Event History” object stores a history of every DACS Event raised by the DACS server.  For each individual type of event (defined above, in the “DACS Server Events” table), the “DACS Event History” stores a list of DACS Server Objects which have recently raised the specific event.

Each event’s history is stored in the form of a circular buffer.  Each history buffer can store up to 255 entries.  For any given event history buffer, an EtherNet/IP-compatible device can retrieve:

- The current index of the most recently-occurring instance of the event.

- Given a desired index; the UID of the DACS Server Object which raised the event

### Class Code

The Class ID of the DACS Event Queue object is 101 (hex 0x65).

### Class Attributes

The “DACS Event History” object provides the following attributes at the “class” level (instance 0):

| Attribute | Access | Name | CIP Data Type | Description |
| --- | --- | --- | --- | --- |
| 0x01 | Get | Revision | UINT | Get the current revision of the class definition. The initial revision of the class is 1. |

### Instances

The Adapter provides only a single instance of the DACS Event History object: instance 1 (hex 0x01).

### Instance Services

The “DACS Event History” object provides object-specific CIP services, providing a means through which to retrieve the index of the ‘most recent’ instance of a given event; as well as a means through which to retrieve specific instances of a given event.  These services are defined below, with a brief description.

Service-specific request data is outlined in the following sections.

| Service Code | Service Name | Description |
| --- | --- | --- |
| 0x4B | Get DACS Event Entry | Retrieve the UID of the DACS object which raised the event with the specified index, in the Event Monitor Assembly. |
| 0x4C | Get Current Index | Retrieve the ‘current index’ of the most recent event entry, in the specified event’s history. |

#### “Get DACS Event Entry” Request Data

The “Get DACS Event Entry” service accepts an 8-bit “Event ID” value, and a desired 8-bit “Index” value, representing the index within the circular buffer from which to retrieve the event data.  The service returns the UID of the DACS Server Object which raised the desired event.  The request data for a “Get DACS Event Entry” service request is defined below:

| Required or Optional | Name | CIP Data type | Description |
| --- | --- | --- | --- |
| Required | Event ID | USINT | The 8-bit identifier of the desired event. For the full list of supported events, refer to the full table: DACS Server Events. |
| Required | Buffer Index | USINT | The 8-bit index – within the event’s circular buffer – of the desired event history entry. |

##### Example

An example “Get DACS Event Entry” service request is outlined below.  This example retrieves UID of the DACS ‘gateway’ object which raised the “GWY_DEVICE_LIST_SIZE Changed” event.  It retrieves the UID from index ‘120’ of the event’s circular buffer.

| Service Code |  | 75 (hex: 0x4B) |  |
| --- | --- | --- | --- |
| Class ID |  | 101 (hex: 0x65) |  |
| Instance Number |  | 1 (hex: 0x01) |  |
| Request Data (Length: 2 bytes) |  |  |  |
| Name | Event ID |  | Buffer Index |
| Raw Data | 08 |  | 78 |
| Value | [USINT] 8 (0x08) (‘GWY_DEVICE_LIST_SIZE Changed’) |  | [USINT] 120 (0x78) (‘Index 120’) |

#### “Get Current Index” Request Data

The “Get Current Index” service accepts an Event ID value, and returns the ‘current index’ of the most recent instance within that event’s circular buffer.  The request data for a “Get Current Index” service request is defined below:

| Required or Optional | Name | CIP Data type | Description |
| --- | --- | --- | --- |
| Required | Event ID | USINT | The 8-bit Event identifier of the desired event history buffer. For the full list of supported events, refer to the table DACS Server Events. |

##### Example

An example “Get Current Index” service request is outlined below.  This example retrieves the most recent index of the DACS “EMERGENCY_OVERRIDE Changed” event.

| Service Code |  | 75 (hex: 0x4B) |
| --- | --- | --- |
| Class ID |  | 101 (hex: 0x65) |
| Instance Number |  | 1 (hex: 0x01) |
| Request Data (Length: 1 byte) |  |  |
| Name | Event ID |  |
| Raw Data | 06 |  |
| Value | [USINT] 6 (0x06) (‘EMERGENCY_OVERRIDE Changed’) |  |

### Event History: Circular Buffer Behavior

Each event type maintains its own circular buffer.  Index 0 (zero) of any buffer is never used; if the reported ‘current index’ of any buffer returns zero, it indicates an empty buffer with no events.

Any reported ‘current index’ with a non-zero value indicates one or more events, stored in the buffer.  Once more than 255 events have been received, the most recent event is placed in index ‘1,’ with previous events stored at index 255, 254, 253, etc.

## Assembly Object: “Event Monitor”

To avoid the inefficient task of constantly ‘polling’ the DACS Event History object for new events, a single assembly is provided through which a PLC may establish a real-time, Class 1 I/O connection.  Each byte within the assembly represents the “Current Index” value of the DACS Server Event, whose ID matches the index of the byte.

Byte index 1 in the assembly contains the current index for the DACS Server Event with ID of “1” (‘GATEWAY_LIST_SIZE Changed’).  Byte index 2 contains the event count for the DACS Server Event with ID of “2” (‘ALERT_LIST_SIZE Changed’), and so on.  Refer to the “DACS Server Events” table, for the complete list of supported events.

The byte at index 0 is not used.  Bytes beyond index 15 are reserved for future use.

### Usage

A PLC or EtherNet/IP-enabled device will monitor the values within this assembly.  When a relevant event count is changed, the PLC will retrieve the relevant event parameters from the “DACS Event History” object, as described in the previous section.

### Class 1 I/O Connection Parameters

A Class 1 “Input-Only” connection can be established with the Event Monitor assembly, using the following connection points:

Originator to Target Connection Point (“Heartbeat”):

- Instance 198 (hex: 0xC6)

- Size: 0

- Run/Idle header: no

Target to Originator Connection Point (“Event Monitor”):

- Instance 100 (hex: 0x64)

- Size: 128

- Run/Idle header: no

# PLC Example Logic

Included with the DACS EtherNet/IP Adapter, a number of PLC example programs have been provided.  These examples illustrate simple use-cases which end-users can build upon or use for reference.

## Common Subroutines

In all example programs, two subroutines are referenced frequently; “EncodeRequest” and “DecodeResponse.”  These subroutines allow a user to quickly ‘pack’ and ‘unpack’ their desired request parameters (and corresponding response values) to and from an simple array of bytes, to be used in the PLC’s “Message” instruction when interacting with the DACS EtherNet/IP Adapter.

### “EncodeRequest” Subroutine

The “EncodeRequest” subroutine takes 4 parameters:

- RequestBlock – This parameter should be the same as the “return” value.  It represents an array of bytes, to be used in a MESSAGE instruction, when requesting data from the DACS Server.

- PropertyID – The ID of the property being retrieved (or assigned).

- TargetUID – The UID string identifying the DACS Object being interacted with.

- Parameter – An optional parameter to be appended to the end of the request block.  For “Get Property” requests, this can be the desired index of an element in an array.  For “Set” requests, this should be the value being assigned to the propery.

It returns the resulting packed block of request data.  The resulting request data should be used in a subsequent MESSAGE instruction.

### “DecodeResponse” Subroutine

The “DecodeResponse” subroutine takes 3 parameters:

- ResponseBlock – This parameter should be the same as the “return” value.  It represents an array of bytes, to be used in a MESSAGE instruction, when requesting data from the DACS Server.

- ResponseType – A string, identifying the data type into which the response block should be parsed.  The subroutine supports the following data type strings:

  - “INT”

  - “DINT”

  - “STRING”

- ResponseBlockReturn – This parameter should be the same as the “return” value.  It contains the resulting parsed data value from the response block, placed into the member associated with the described “ResponseType.”

It returns a structure containing the various supported data types.  The parsed value will be located in the member with the prescribed data type (“ResponseType”).

## Example 01: Set a light level to 100%, when a motion sensor is triggered

In this simple example, suppose a PLC wants to turn a specific light on, whenever an accompanying motion sensor detects motion.

Assume:

- The light has a UID of “MyExampleLight”

- The sensor has a UID of “MyExampleSensor”

This example is implemented with the following logic:

- Read the input data from the DACS EtherNet/IP Adapter, over the network.

- Check the value of the input byte at index 7 (“Motion Sensed”).

- When the value changes:

  - Query the “DACS Event History” object: Service 0x4B, Class 0x65, Instance 1.  Using a MESSAGE instruction, we request the DACS “Motion Sensed” (value: 0x07) event history, using the value we retrieved from the input data, in the previous step.  This retrieves the UID of the device which raised the most recent instance of the “Motion Sensed” event.

    - Since requests for event data consist of only 2 bytes, use the MOV and COP instructions to copy the desired “Event ID” and “Event Index” to a request structure.

  - Use the “DecodeResponse” subroutine to parse the response data.  Examine the UID of the resulting event-raiser, in the response data.  If the UID matches our desired sensor (“MyExampleSensor”):

  - Send a request to the “DACS Control” object: Service 0x4C, Class 0x64, Instance 1.  The request data should contain the desired property we wish to affect UID of the desired light (“MyExampleLight”), followed by an 8-bit unsigned integer, setting the light level to max (255).  Use the “EncodeRequest” subroutine to pack the parameters into the request structure.

### Using This Example

Using Studio 5000 designer, Import the provided file: “Example01_MotionSensed.L5K.”

Before downloading the example logic to the PLC, ensure the device IP Addresses are updated, to point at the correct target devices.  Also ensure that the ‘target’ sensor and light UIDs are updated, to reflect valid UIDs of actual devices on your test setup.  These UIDs can be assigned via the PLC Tags: “SensorUID” and “LightUID.”

With the logic running on the PLC, you will need to manually set the light level of the target light to 0%.  Once the light has been manually turned off, perform some motion in front of the target motion sensor.  The PLC should automatically turn the target light on, at 100% strength.

## Example 02: Determine Which ‘Group’ Consumes the Most Power

In this example, an EtherNet/IP-compatible device wants to enumerate through the list of all “Groups” defined by the DACS Server, and identify the group consuming the most power.

This example is implemented with the following logic:

- Determine the number of groups defined by the Lighting System:

  - Using the “EncodeRequest” subroutine, encode a request for Property 0x0007 (“Group list size”), from the reserved Server UID “Lighting-System.”

  - Query the “DACS Control” object: Service 0x4B, Class 0x64, Instance 1, using the request data encoded in the previous step.

  - Decode the response.  The returned value represents the total number of Groups contained in the Lighting System

- Find the Group with the highest power consumption.

  - For each index [0 – “Group list size”], determined in the previous step:

    - Retrieve the UID of the ‘current group’:

      - Encode a request for property 0x0008 (“Group list: get element”), from the reserved server UID “Lighting-System.”  In the ‘parameter’ field, include the desired, current index.

      - Query the “DACS Control” object: Service 0x4B, Class 0x64, Instance 1, using the request block created in the previous step.

      - Decode the response.  The returned value represents the UID of the Group located at the current index.

    - Using the UID of the current group, retrieve the current power consumption:

      - Encode a request for property 0x0702 (“Group power consumed”), from the UID retrieved in the previous step.

      - Query the “DACS Control” object: Service 0x4B, Class 0x64, Instance 1, using the request data from the previous step.

      - The returned value represents the current power consumption of the current group.

    - If the power consumed is greater than the currently-found “Max” value, then save the UID and Power Consumption as the new “Max” value.

### Using This Example

Using Studio 5000 designer, Import the provided file: “Example02_DetectGroupPowerConsumption.L5K.”

Before downloading the example logic to the PLC, ensure the device IP Addresses are updated, to point at the correct target devices.

With the logic running on the PLC, you will need to manually ‘toggle’ the PLC’s control bit, labeled “StartRequest.”  Each time this bit is turned ‘on,’ the PLC will run through the list of groups, determining which group consumes the most power and storing the result in the tag: “MAX_GROUP_UID.”

Using the DACS WebUI, fiddle with the various light levels of your groups.  Each time you change a group’s light level, trigger the “StartRequest” bit on the PLC to update the determined ‘highest consumer.’

# Appendix A: Enumerations

## Device Sub-Types

| Value | Name |
| --- | --- |
| 0x01 | Light |
| 0x02 | Basic Light |
| 0x03 | Sensor |
| 0x04 | Gateway |

## Sensor Sub-Types

| Value | Name |
| --- | --- |
| 0x01 | WOCC Sensor |
| 0x02 | WDLH Sensor |

## Group WDLH Modes

| Value | Name |
| --- | --- |
| 0x01 | Avg. Mode |
| 0x02 | Min Mode |
| 0x03 | Max Mode |

## Alert Types

| Value | Name |
| --- | --- |
| 0x01 | Advisory |
| 0x02 | Warning |
| 0x03 | Error |

## Alert States

| Value | Name |
| --- | --- |
| 0x01 | New |
| 0x02 | Acknowledged |
| 0x03 | Delete |